## System Curve
System Curve Input
Instructions: Input data to shaded cells only. Remaining cells are calculated
Find Minor Loss Coefficients Here
Enter Per NAVD88 | Invert at Discharge | 8.62
| Impeller Eye El | -13.9 |  |  |  | Force Main 1 |  | Force main 2 |  | Misc Fittings 1 |  | Misc Fittings 2 |  |  |  | Common Force Main Fittings
| WW Transducer Tip El | -15.39 |  |  |  | 10 |  | 12 |  | 10 |  | 8 |  | Fitting Type | Header |  | LR Ell | DDGV | 10x12 Ell | DDGV | Tee-Line | 90 Bend | Exit |  |  |  |  | FM 1 | FM 2
|  |  | Static Head |  |  | Velocity, ft/s | V2/2g, ft | Velocity, ft/s | V2/2g, ft | Velocity, ft/s | V2/2g, ft | Velocity, ft/s | V2/2g, ft | Size, in |  | 10 | 10 | 10 | 12 | 12 | 12 | 12 | 12 | 10 | 10 | 10 | FM Minor Loss, ft | Friction Losses, ft | Friction Losses, ft | TDH Lead Off, ft | TDH Lead On, ft | TDH Lead+Lag Off, ft | TDH Lead+Lag On, ft | TDH Overflow, ft
Enter Per Wonderware/ SCADA | Lead Off Setpoint | 1.21 | 22.8 | [10 empty] | K |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
| Lag Off Setpoint | 1.21 | 22.8 | Flow Rate, GPM | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8 | 15.57 | 22.8 | 15.22 | 2.01
| Level Control Setpoint | 8.44 | 15.57 |  | 200 | 0.81669 | 0.010357 | 0.56714 | 0.0049946 | 0.81669 | 0.010357 | 1.2761 | 0.025285 |  |  | 0.0051784 | 0.0051784 | 0.0051784 | 0.0024973 | 0.0024973 | 0.0024973 | 0.0024973 | 0.0024973 | 0.0051784 | 0.0051784 | 0.0051784 | 0.043557 | 0.0056659 | 0.0066856 | 22.8559 | 15.6259 | 22.8559 | 15.2759 | 2.0659
| Lag On Setpoint | 8.79 | 15.22 |  | 400 | 1.6334 | 0.041427 | 1.1343 | 0.019978 | 1.6334 | 0.041427 | 2.5522 | 0.10114 |  |  | 0.020714 | 0.020714 | 0.020714 | 0.0099892 | 0.0099892 | 0.0099892 | 0.0099892 | 0.0099892 | 0.020714 | 0.020714 | 0.020714 | 0.17423 | 0.020426 | 0.024102 | 23.0188 | 15.7888 | 23.0188 | 15.4388 | 2.2288
| Overflow Setpoint | 22 | 2.01 |  | 600 | 2.4501 | 0.093211 | 1.7014 | 0.044952 | 2.4501 | 0.093211 | 3.8282 | 0.22757 |  |  | 0.046606 | 0.046606 | 0.046606 | 0.022476 | 0.022476 | 0.022476 | 0.022476 | 0.022476 | 0.046606 | 0.046606 | 0.046606 | 0.39201 | 0.043246 | 0.051029 | 23.2863 | 16.0563 | 23.2863 | 15.7063 | 2.4963
Response Time | High WW Setpoint | 12.86 |  |  | 800 | 3.2668 | 0.16571 | 2.2686 | 0.079914 | 3.2668 | 0.16571 | 5.1043 | 0.40456 |  |  | 0.082855 | 0.082855 | 0.082855 | 0.039957 | 0.039957 | 0.039957 | 0.039957 | 0.039957 | 0.082855 | 0.082855 | 0.082855 | 0.69691 | 0.073634 | 0.086887 | 23.6574 | 16.4274 | 23.6574 | 16.0774 | 2.8674
| WW Plan Area | 180 |  |  | 1000 | 4.0834 | 0.25892 | 2.8357 | 0.12487 | 4.0834 | 0.25892 | 6.3804 | 0.63213 |  |  | 0.12946 | 0.12946 | 0.12946 | 0.062433 | 0.062433 | 0.062433 | 0.062433 | 0.062433 | 0.12946 | 0.12946 | 0.12946 | 1.0889 | 0.11127 | 0.13129 | 24.1315 | 16.9015 | 24.1315 | 16.5515 | 3.3415
| WW Storage Volume | 12306.096 | gal |  | 1200 | 4.9001 | 0.37285 | 3.4029 | 0.17981 | 4.9001 | 0.37285 | 7.6565 | 0.91027 |  |  | 0.18642 | 0.18642 | 0.18642 | 0.089903 | 0.089903 | 0.089903 | 0.089903 | 0.089903 | 0.18642 | 0.18642 | 0.18642 | 1.5681 | 0.1559 | 0.18396 | 24.7079 | 17.4779 | 24.7079 | 17.1279 | 3.9179
| Avg Inflow Rate, wet/dry | 800 | 300 |  | 1400 | 5.7168 | 0.50748 | 3.97 | 0.24474 | 5.7168 | 0.50748 | 8.9325 | 1.239 |  |  | 0.25374 | 0.25374 | 0.25374 | 0.12237 | 0.12237 | 0.12237 | 0.12237 | 0.12237 | 0.25374 | 0.25374 | 0.25374 | 2.1343 | 0.20735 | 0.24467 | 25.3863 | 18.1563 | 25.3863 | 17.8063 | 4.5963
| Response Time, hr | 0.25638 | 0.68367 |  | 1600 | 6.5335 | 0.66284 | 4.5372 | 0.31966 | 6.5335 | 0.66284 | 10.2086 | 1.6183 |  |  | 0.33142 | 0.33142 | 0.33142 | 0.15983 | 0.15983 | 0.15983 | 0.15983 | 0.15983 | 0.33142 | 0.33142 | 0.33142 | 2.7876 | 0.26545 | 0.31323 | 26.1663 | 18.9363 | 26.1663 | 18.5863 | 5.3763
Suction Piping | Material | CI |  |  | 1800 | 7.3502 | 0.8389 | 5.1043 | 0.40456 | 7.3502 | 0.8389 | 11.4847 | 2.0481 |  |  | 0.41945 | 0.41945 | 0.41945 | 0.20228 | 0.20228 | 0.20228 | 0.20228 | 0.20228 | 0.41945 | 0.41945 | 0.41945 | 3.5281 | 0.33008 | 0.38949 | 27.0477 | 19.8177 | 27.0477 | 19.4677 | 6.2577
| Age | 51 |  |  | 2000 | 8.1669 | 1.0357 | 5.6714 | 0.49946 | 8.1669 | 1.0357 | 12.7608 | 2.5285 |  |  | 0.51784 | 0.51784 | 0.51784 | 0.24973 | 0.24973 | 0.24973 | 0.24973 | 0.24973 | 0.51784 | 0.51784 | 0.51784 | 4.3557 | 0.40112 | 0.47331 | 28.0301 | 20.8001 | 28.0301 | 20.4501 | 7.2401
| Hazen-Williams 'C' | 100 |  |  | 2200 | 8.9836 | 1.2532 | 6.2386 | 0.60435 | 8.9836 | 1.2532 | 14.0368 | 3.0595 |  |  | 0.62659 | 0.62659 | 0.62659 | 0.30217 | 0.30217 | 0.30217 | 0.30217 | 0.30217 | 0.62659 | 0.62659 | 0.62659 | 5.2704 | 0.47846 | 0.56457 | 29.1134 | 21.8834 | 29.1134 | 21.5334 | 8.3234
| Diameter | 10 |  |  | 2400 | 9.8003 | 1.4914 | 6.8057 | 0.71922 | 9.8003 | 1.4914 | 15.3129 | 3.6411 |  |  | 0.74569 | 0.74569 | 0.74569 | 0.35961 | 0.35961 | 0.35961 | 0.35961 | 0.35961 | 0.74569 | 0.74569 | 0.74569 | 6.2722 | 0.56202 | 0.66318 | 30.2974 | 23.0674 | 30.2974 | 22.7174 | 9.5074
| Suction Length, ft | 2 |  |  | 2600 | 10.6169 | 1.7503 | 7.3729 | 0.84409 | 10.6169 | 1.7503 | 16.589 | 4.2732 |  |  | 0.87515 | 0.87515 | 0.87515 | 0.42204 | 0.42204 | 0.42204 | 0.42204 | 0.42204 | 0.87515 | 0.87515 | 0.87515 | 7.3611 | 0.65173 | 0.76902 | 31.5819 | 24.3519 | 31.5819 | 24.0019 | 10.7919
| Suction Area, ft2 | 0.54542 |  |  | 2800 | 11.4336 | 2.0299 | 7.94 | 0.97894 | 11.4336 | 2.0299 | 17.8651 | 4.9559 |  |  | 1.015 | 1.015 | 1.015 | 0.48947 | 0.48947 | 0.48947 | 0.48947 | 0.48947 | 1.015 | 1.015 | 1.015 | 8.5372 | 0.74749 | 0.88202 | 32.9667 | 25.7367 | 32.9667 | 25.3867 | 12.1767
Individual Pump Discharge Piping | Material | CI |  |  | 3000 | 12.2503 | 2.3303 | 8.5072 | 1.1238 | 12.2503 | 2.3303 | 19.1411 | 5.6892 |  |  | 1.1651 | 1.1651 | 1.1651 | 0.56189 | 0.56189 | 0.56189 | 0.56189 | 0.56189 | 1.1651 | 1.1651 | 1.1651 | 9.8003 | 0.84926 | 1.0021 | 34.4517 | 27.2217 | 34.4517 | 26.8717 | 13.6617
| Age | 51
| Hazen-Williams 'C' | 100 | [8 empty] | Note: for reducing/increasing fittings, use the exit size
| Diameter | 10
| Length, ft | 2
| Area, ft2 | 0.54542 | [13 empty] | Suction Fittings |  |  |  |  | Sum of Suction Minor Losses |  |  |  | Individual Pump Discharge Fittings | [5 empty] | Sum of Discharge Minor Losses
Force Main Segment 1 | Material | CI | [12 empty] | Fitting Type | Entrance | DDGV | 10x8 Red | 90 Ell |  |  | Suction Friction Loss | Sum of Suction Losses | Pump | 6x8 Ell | SCV | Plug V | 8x10 Ell | Tee-Line | Tee-Line |  | Sum of Discharge Friction Loss | Sum of Discharge Losses | Sum of all Pump Unit Losses
| Age | 51 | [12 empty] | Size, in | 12 | 10 | 12 | 12 | 12 |  |  |  |  | 8 | 12 | 12 | 12 | 12 | 12
| Hazen-Williams 'C' | 100 | [12 empty] | K | 1 | 0.5 | 0.5 | 0.5 | [5 empty] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
| Diameter | 10
| Length, ft | 11.16 | [10 empty] | %Speed | RPM | Flows
| Area, ft2 | 0.54542 | [10 empty] | 100% | 1900 RPM | 960 | 0.11508 | 0.11931 | 0.057538 | 0.057538 | 0 | 0.34946 | 0.01849 | 0.36795 |  | 0.29129 | 0.057538 | 0.057538 | 0.057538 | 0.057538 | 0.057538 | 0.57898 | 0.01849 | 0.59747 | 0.96542
Force Main Segment 2 | Material | CI | [12 empty] | 1440 | 0.25892 | 0.26845 | 0.12946 | 0.12946 | 0 | 0.78629 | 0.039147 | 0.82544 |  | 0.65539 | 0.12946 | 0.12946 | 0.12946 | 0.12946 | 0.12946 | 1.3027 | 0.039147 | 1.3418 | 2.1673
| Age | 51 | [12 empty] | 1920 | 0.4603 | 0.47724 | 0.23015 | 0.23015 | 0 | 1.3978 | 0.066656 | 1.4645 |  | 1.1651 | 0.23015 | 0.23015 | 0.23015 | 0.23015 | 0.23015 | 2.3159 | 0.066656 | 2.3826 | 3.8471
| Hazen-Williams 'C' | 100 | [12 empty] | 2400 | 0.71922 | 0.74569 | 0.35961 | 0.35961 | 0 | 2.1841 | 0.10072 | 2.2849 |  | 1.8205 | 0.35961 | 0.35961 | 0.35961 | 0.35961 | 0.35961 | 3.6186 | 0.10072 | 3.7193 | 6.0042
| Diameter | 12 | [12 empty] | 2880 | 1.0357 | 1.0738 | 0.51784 | 0.51784 | 0 | 3.1452 | 0.14113 | 3.2863 |  | 2.6216 | 0.51784 | 0.51784 | 0.51784 | 0.51784 | 0.51784 | 5.2108 | 0.14113 | 5.3519 | 8.6382
| Length | 32 | [10 empty] | 95% | 1805 RPM | 912 | 0.10386 | 0.10768 | 0.051928 | 0.051928 | 0 | 0.31539 | 0.016816 | 0.33221 |  | 0.26289 | 0.051928 | 0.051928 | 0.051928 | 0.051928 | 0.051928 | 0.52253 | 0.016816 | 0.53934 | 0.87155 | 95
| Area, ft2 | 0.7854 | [12 empty] | 1368 | 0.23368 | 0.24228 | 0.11684 | 0.11684 | 0 | 0.70963 | 0.035603 | 0.74523 |  | 0.59149 | 0.11684 | 0.11684 | 0.11684 | 0.11684 | 0.11684 | 1.1757 | 0.035603 | 1.2113 | 1.9565
| Total Length, ft | 47.16 | [12 empty] | 1824 | 0.41542 | 0.43071 | 0.20771 | 0.20771 | 0 | 1.2616 | 0.060621 | 1.3222 |  | 1.0515 | 0.20771 | 0.20771 | 0.20771 | 0.20771 | 0.20771 | 2.0901 | 0.060621 | 2.1507 | 3.4729
[15 empty] | 2280 | 0.6491 | 0.67299 | 0.32455 | 0.32455 | 0 | 1.9712 | 0.091603 | 2.0628 |  | 1.643 | 0.32455 | 0.32455 | 0.32455 | 0.32455 | 0.32455 | 3.2658 | 0.091603 | 3.3574 | 5.4202
[15 empty] | 2736 | 0.9347 | 0.9691 | 0.46735 | 0.46735 | 0 | 2.8385 | 0.12835 | 2.9669 |  | 2.366 | 0.46735 | 0.46735 | 0.46735 | 0.46735 | 0.46735 | 4.7027 | 0.12835 | 4.8311 | 7.7979
[13 empty] | 90% | 1710 RPM | 864 | 0.093211 | 0.096642 | 0.046606 | 0.046606 | 0 | 0.28306 | 0.015215 | 0.29828 |  | 0.23594 | 0.046606 | 0.046606 | 0.046606 | 0.046606 | 0.046606 | 0.46897 | 0.015215 | 0.48419 | 0.78247 | 90
[15 empty] | 1296 | 0.20973 | 0.21744 | 0.10486 | 0.10486 | 0 | 0.6369 | 0.032214 | 0.66911 |  | 0.53087 | 0.10486 | 0.10486 | 0.10486 | 0.10486 | 0.10486 | 1.0552 | 0.032214 | 1.0874 | 1.7565
[15 empty] | 1728 | 0.37285 | 0.38657 | 0.18642 | 0.18642 | 0 | 1.1323 | 0.054851 | 1.1871 |  | 0.94377 | 0.18642 | 0.18642 | 0.18642 | 0.18642 | 0.18642 | 1.8759 | 0.054851 | 1.9307 | 3.1178
[15 empty] | 2160 | 0.58257 | 0.60401 | 0.29129 | 0.29129 | 0 | 1.7692 | 0.082884 | 1.852 |  | 1.4746 | 0.29129 | 0.29129 | 0.29129 | 0.29129 | 0.29129 | 2.9311 | 0.082884 | 3.0139 | 4.866
[15 empty] | 2592 | 0.8389 | 0.86977 | 0.41945 | 0.41945 | 0 | 2.5476 | 0.11613 | 2.6637 |  | 2.1235 | 0.41945 | 0.41945 | 0.41945 | 0.41945 | 0.41945 | 4.2207 | 0.11613 | 4.3369 | 7.0006
[13 empty] | 85% | 1615 RPM | 816 | 0.083142 | 0.086202 | 0.041571 | 0.041571 | 0 | 0.25249 | 0.013689 | 0.26618 |  | 0.21045 | 0.041571 | 0.041571 | 0.041571 | 0.041571 | 0.041571 | 0.41831 | 0.013689 | 0.432 | 0.69817 | 85
[15 empty] | 1224 | 0.18707 | 0.19395 | 0.093535 | 0.093535 | 0 | 0.56809 | 0.028982 | 0.59708 |  | 0.47352 | 0.093535 | 0.093535 | 0.093535 | 0.093535 | 0.093535 | 0.9412 | 0.028982 | 0.97018 | 1.5673
[15 empty] | 1632 | 0.33257 | 0.34481 | 0.16628 | 0.16628 | 0 | 1.0099 | 0.049347 | 1.0593 |  | 0.84182 | 0.16628 | 0.16628 | 0.16628 | 0.16628 | 0.16628 | 1.6732 | 0.049347 | 1.7226 | 2.7819
[15 empty] | 2040 | 0.51964 | 0.53876 | 0.25982 | 0.25982 | 0 | 1.578 | 0.074567 | 1.6526 |  | 1.3153 | 0.25982 | 0.25982 | 0.25982 | 0.25982 | 0.25982 | 2.6144 | 0.074567 | 2.689 | 4.3416
[15 empty] | 2448 | 0.74828 | 0.77582 | 0.37414 | 0.37414 | 0 | 2.2724 | 0.10448 | 2.3769 |  | 1.8941 | 0.37414 | 0.37414 | 0.37414 | 0.37414 | 0.37414 | 3.7648 | 0.10448 | 3.8693 | 6.2461
[13 empty] | 80% | 1520 RPM | 768 | 0.073649 | 0.076359 | 0.036824 | 0.036824 | 0 | 0.22366 | 0.012236 | 0.23589 |  | 0.18642 | 0.036824 | 0.036824 | 0.036824 | 0.036824 | 0.036824 | 0.37054 | 0.012236 | 0.38278 | 0.61867 | 80
[15 empty] | 1152 | 0.16571 | 0.17181 | 0.082855 | 0.082855 | 0 | 0.50323 | 0.025907 | 0.52913 |  | 0.41945 | 0.082855 | 0.082855 | 0.082855 | 0.082855 | 0.082855 | 0.83372 | 0.025907 | 0.85963 | 1.3888
[15 empty] | 1536 | 0.29459 | 0.30544 | 0.1473 | 0.1473 | 0 | 0.89462 | 0.044112 | 0.93874 |  | 0.74569 | 0.1473 | 0.1473 | 0.1473 | 0.1473 | 0.1473 | 1.4822 | 0.044112 | 1.5263 | 2.465
[15 empty] | 1920 | 0.4603 | 0.47724 | 0.23015 | 0.23015 | 0 | 1.3978 | 0.066656 | 1.4645 |  | 1.1651 | 0.23015 | 0.23015 | 0.23015 | 0.23015 | 0.23015 | 2.3159 | 0.066656 | 2.3826 | 3.8471
[15 empty] | 2304 | 0.66284 | 0.68723 | 0.33142 | 0.33142 | 0 | 2.0129 | 0.093395 | 2.1063 |  | 1.6778 | 0.33142 | 0.33142 | 0.33142 | 0.33142 | 0.33142 | 3.3349 | 0.093395 | 3.4283 | 5.5346
[13 empty] | 75% | 1425 RPM | 720 | 0.06473 | 0.067112 | 0.032365 | 0.032365 | 0 | 0.19657 | 0.010859 | 0.20743 |  | 0.16385 | 0.032365 | 0.032365 | 0.032365 | 0.032365 | 0.032365 | 0.32567 | 0.010859 | 0.33653 | 0.54396 | 75
|  | Size Index | [12 empty] | 1080 | 0.14564 | 0.151 | 0.072821 | 0.072821 | 0 | 0.44229 | 0.022991 | 0.46528 |  | 0.36866 | 0.072821 | 0.072821 | 0.072821 | 0.072821 | 0.072821 | 0.73277 | 0.022991 | 0.75576 | 1.221
|  | 10 | [12 empty] | 1440 | 0.25892 | 0.26845 | 0.12946 | 0.12946 | 0 | 0.78629 | 0.039147 | 0.82544 |  | 0.65539 | 0.12946 | 0.12946 | 0.12946 | 0.12946 | 0.12946 | 1.3027 | 0.039147 | 1.3418 | 2.1673
|  | 10 | [12 empty] | 1800 | 0.40456 | 0.41945 | 0.20228 | 0.20228 | 0 | 1.2286 | 0.059154 | 1.2877 |  | 1.0241 | 0.20228 | 0.20228 | 0.20228 | 0.20228 | 0.20228 | 2.0355 | 0.059154 | 2.0946 | 3.3823
|  | 12 | [12 empty] | 2160 | 0.58257 | 0.60401 | 0.29129 | 0.29129 | 0 | 1.7692 | 0.082884 | 1.852 |  | 1.4746 | 0.29129 | 0.29129 | 0.29129 | 0.29129 | 0.29129 | 2.9311 | 0.082884 | 3.0139 | 4.866
|  | 8 | [10 empty] | 70% | 1330 RPM | 672 | 0.056387 | 0.058462 | 0.028194 | 0.028194 | 0 | 0.17124 | 0.0095579 | 0.18079 |  | 0.14273 | 0.028194 | 0.028194 | 0.028194 | 0.028194 | 0.028194 | 0.2837 | 0.0095579 | 0.29326 | 0.47405 | 70
[15 empty] | 1008 | 0.12687 | 0.13154 | 0.063436 | 0.063436 | 0 | 0.38528 | 0.020236 | 0.40552 |  | 0.32114 | 0.063436 | 0.063436 | 0.063436 | 0.063436 | 0.063436 | 0.63832 | 0.020236 | 0.65856 | 1.0641
[15 empty] | 1344 | 0.22555 | 0.23385 | 0.11277 | 0.11277 | 0 | 0.68495 | 0.034456 | 0.7194 |  | 0.57092 | 0.11277 | 0.11277 | 0.11277 | 0.11277 | 0.11277 | 1.1348 | 0.034456 | 1.1692 | 1.8887
[15 empty] | 1680 | 0.35242 | 0.36539 | 0.17621 | 0.17621 | 0 | 1.0702 | 0.052066 | 1.1223 |  | 0.89206 | 0.17621 | 0.17621 | 0.17621 | 0.17621 | 0.17621 | 1.7731 | 0.052066 | 1.8252 | 2.9475
[15 empty] | 2016 | 0.50748 | 0.52616 | 0.25374 | 0.25374 | 0 | 1.5411 | 0.072952 | 1.6141 |  | 1.2846 | 0.25374 | 0.25374 | 0.25374 | 0.25374 | 0.25374 | 2.5533 | 0.072952 | 2.6262 | 4.2403
[13 empty] | 65% | 1235 RPM | 624 | 0.04862 | 0.050409 | 0.02431 | 0.02431 | 0 | 0.14765 | 0.0083334 | 0.15598 |  | 0.12307 | 0.02431 | 0.02431 | 0.02431 | 0.02431 | 0.02431 | 0.24462 | 0.0083334 | 0.25295 | 0.40893 | 65
[15 empty] | 936 | 0.10939 | 0.11342 | 0.054697 | 0.054697 | 0 | 0.33221 | 0.017644 | 0.34985 |  | 0.2769 | 0.054697 | 0.054697 | 0.054697 | 0.054697 | 0.054697 | 0.55039 | 0.017644 | 0.56803 | 0.91788
[15 empty] | 1248 | 0.19448 | 0.20163 | 0.097239 | 0.097239 | 0 | 0.59059 | 0.030042 | 0.62063 |  | 0.49227 | 0.097239 | 0.097239 | 0.097239 | 0.097239 | 0.097239 | 0.97847 | 0.030042 | 1.0085 | 1.6291
[15 empty] | 1560 | 0.30387 | 0.31505 | 0.15194 | 0.15194 | 0 | 0.9228 | 0.045395 | 0.96819 |  | 0.76918 | 0.15194 | 0.15194 | 0.15194 | 0.15194 | 0.15194 | 1.5289 | 0.045395 | 1.5743 | 2.5424
[15 empty] | 1872 | 0.43758 | 0.45368 | 0.21879 | 0.21879 | 0 | 1.3288 | 0.063606 | 1.3924 |  | 1.1076 | 0.21879 | 0.21879 | 0.21879 | 0.21879 | 0.21879 | 2.2016 | 0.063606 | 2.2652 | 3.6576
[13 empty] | 60% | 1140 RPM | 576 | 0.041427 | 0.042952 | 0.020714 | 0.020714 | 0 | 0.12581 | 0.0071864 | 0.13299 |  | 0.10486 | 0.020714 | 0.020714 | 0.020714 | 0.020714 | 0.020714 | 0.20843 | 0.0071864 | 0.21562 | 0.34861 | 60
[15 empty] | 864 | 0.093211 | 0.096642 | 0.046606 | 0.046606 | 0 | 0.28306 | 0.015215 | 0.29828 |  | 0.23594 | 0.046606 | 0.046606 | 0.046606 | 0.046606 | 0.046606 | 0.46897 | 0.015215 | 0.48419 | 0.78247
[15 empty] | 1152 | 0.16571 | 0.17181 | 0.082855 | 0.082855 | 0 | 0.50323 | 0.025907 | 0.52913 |  | 0.41945 | 0.082855 | 0.082855 | 0.082855 | 0.082855 | 0.082855 | 0.83372 | 0.025907 | 0.85963 | 1.3888
[15 empty] | 1440 | 0.25892 | 0.26845 | 0.12946 | 0.12946 | 0 | 0.78629 | 0.039147 | 0.82544 |  | 0.65539 | 0.12946 | 0.12946 | 0.12946 | 0.12946 | 0.12946 | 1.3027 | 0.039147 | 1.3418 | 2.1673
[15 empty] | 1728 | 0.37285 | 0.38657 | 0.18642 | 0.18642 | 0 | 1.1323 | 0.054851 | 1.1871 |  | 0.94377 | 0.18642 | 0.18642 | 0.18642 | 0.18642 | 0.18642 | 1.8759 | 0.054851 | 1.9307 | 3.1178
[13 empty] | 55% | 1045 RPM | 528 | 0.03481 | 0.036091 | 0.017405 | 0.017405 | 0 | 0.10571 | 0.0061179 | 0.11183 |  | 0.088114 | 0.017405 | 0.017405 | 0.017405 | 0.017405 | 0.017405 | 0.17514 | 0.0061179 | 0.18126 | 0.29309 | 55
[15 empty] | 792 | 0.078323 | 0.081206 | 0.039162 | 0.039162 | 0 | 0.23785 | 0.012953 | 0.25081 |  | 0.19826 | 0.039162 | 0.039162 | 0.039162 | 0.039162 | 0.039162 | 0.39407 | 0.012953 | 0.40702 | 0.65782
[15 empty] | 1056 | 0.13924 | 0.14437 | 0.069621 | 0.069621 | 0 | 0.42285 | 0.022055 | 0.4449 |  | 0.35246 | 0.069621 | 0.069621 | 0.069621 | 0.069621 | 0.069621 | 0.70056 | 0.022055 | 0.72262 | 1.1675
[15 empty] | 1320 | 0.21757 | 0.22557 | 0.10878 | 0.10878 | 0 | 0.6607 | 0.033327 | 0.69403 |  | 0.55071 | 0.10878 | 0.10878 | 0.10878 | 0.10878 | 0.10878 | 1.0946 | 0.033327 | 1.128 | 1.822
[15 empty] | 1584 | 0.31329 | 0.32482 | 0.15665 | 0.15665 | 0 | 0.95141 | 0.046696 | 0.99811 |  | 0.79303 | 0.15665 | 0.15665 | 0.15665 | 0.15665 | 0.15665 | 1.5763 | 0.046696 | 1.623 | 2.6211
[13 empty] | 50% | 950 RPM | 480 | 0.028769 | 0.029828 | 0.014384 | 0.014384 | 0 | 0.087366 | 0.0051289 | 0.092495 |  | 0.072821 | 0.014384 | 0.014384 | 0.014384 | 0.014384 | 0.014384 | 0.14474 | 0.0051289 | 0.14987 | 0.24237 | 50
[15 empty] | 720 | 0.06473 | 0.067112 | 0.032365 | 0.032365 | 0 | 0.19657 | 0.010859 | 0.20743 |  | 0.16385 | 0.032365 | 0.032365 | 0.032365 | 0.032365 | 0.032365 | 0.32567 | 0.010859 | 0.33653 | 0.54396
[15 empty] | 960 | 0.11508 | 0.11931 | 0.057538 | 0.057538 | 0 | 0.34946 | 0.01849 | 0.36795 |  | 0.29129 | 0.057538 | 0.057538 | 0.057538 | 0.057538 | 0.057538 | 0.57898 | 0.01849 | 0.59747 | 0.96542
[15 empty] | 1200 | 0.17981 | 0.18642 | 0.089903 | 0.089903 | 0 | 0.54603 | 0.027939 | 0.57397 |  | 0.45513 | 0.089903 | 0.089903 | 0.089903 | 0.089903 | 0.089903 | 0.90465 | 0.027939 | 0.93259 | 1.5066
[15 empty] | 1440 | 0.25892 | 0.26845 | 0.12946 | 0.12946 | 0 | 0.78629 | 0.039147 | 0.82544 |  | 0.65539 | 0.12946 | 0.12946 | 0.12946 | 0.12946 | 0.12946 | 1.3027 | 0.039147 | 1.3418 | 2.1673
Note on C34: Nofziger, Jesse: Discharge piping, size 1

## VS Pump Data
Variable Speed Pump Data
Make
Model
Impeller Size |  |  | in
Min Speed |  |  | rpm
Max Speed |  | 1900 | rpm
Design Speed |  |  | rpm
BEC |  | 3400 | GPM
Min Flow (30%) |  | 1020 | GPM
Min Flow (50%) |  | 1700 | GPM
Raw Pump Data
Note: Values calculated from affinity laws. Values in red are outside the recommended performance envelope. Values are not derated for header loss
| Single Pump | 100% | Max | 95% | Max | 90% | Max | 85% | Max | 80% | Max | 75% | Max | 70% | Max | 65% | Max | 60% | Max | 55% | Max | 50% | Max
|  | 1900 | RPM | 1805 | RPM | 1710 | RPM | 1615 | RPM | 1520 | RPM | 1425 | RPM | 1330 | RPM | 1235 | RPM | 1140 | RPM | 1045 | RPM | 950 | RPM
|  | Flow (GPM) | Head (ft) | Flow (GPM) | Head (ft) | Flow (GPM) | Head (ft) | Flow (GPM) | Head (ft) | Flow (GPM) | Head (ft) | Flow (GPM) | Head (ft) | Flow (GPM) | Head (ft) | Flow (GPM) | Head (ft) | Flow (GPM) | Head (ft) | Flow (GPM) | Head (ft) | Flow (GPM) | Head (ft)
|  | 960 | 67 | 912 | 60.4675 | 864 | 54.27 | 816 | 48.4075 | 768 | 42.88 | 720 | 37.6875 | 672 | 32.83 | 624 | 28.3075 | 576 | 24.12 | 528 | 20.2675 | 480 | 16.75
|  | 1440 | 56.7 | 1368 | 51.1718 | 1296 | 45.927 | 1224 | 40.9657 | 1152 | 36.288 | 1080 | 31.8938 | 1008 | 27.783 | 936 | 23.9558 | 864 | 20.412 | 792 | 17.1518 | 720 | 14.175
|  | 1920 | 46 | 1824 | 41.515 | 1728 | 37.26 | 1632 | 33.235 | 1536 | 29.44 | 1440 | 25.875 | 1344 | 22.54 | 1248 | 19.435 | 1152 | 16.56 | 1056 | 13.915 | 960 | 11.5
|  | 2400 | 35.5 | 2280 | 32.0388 | 2160 | 28.755 | 2040 | 25.6487 | 1920 | 22.72 | 1800 | 19.9688 | 1680 | 17.395 | 1560 | 14.9987 | 1440 | 12.78 | 1320 | 10.7388 | 1200 | 8.875
|  | 2880 | 23.2 | 2736 | 20.938 | 2592 | 18.792 | 2448 | 16.762 | 2304 | 14.848 | 2160 | 13.05 | 2016 | 11.368 | 1872 | 9.802 | 1728 | 8.352 | 1584 | 7.018 | 1440 | 5.8
| Dual Pump | 100% | Max | 95% | Max | 90% | Max | 85% | Max | 80% | Max | 75% | Max | 70% | Max | 65% | Max | 60% | Max | 55% | Max | 50% | Max
|  | 1900 | RPM | 1805 | RPM | 1710 | RPM | 1615 | RPM | 1520 | RPM | 1425 | RPM | 1330 | RPM | 1235 | RPM | 1140 | RPM | 1045 | RPM | 950 | RPM
|  | Flow (GPM) | Head (ft) | Flow (GPM) | Head (ft) | Flow (GPM) | Head (ft) | Flow (GPM) | Head (ft) | Flow (GPM) | Head (ft) | Flow (GPM) | Head (ft) | Flow (GPM) | Head (ft) | Flow (GPM) | Head (ft) | Flow (GPM) | Head (ft) | Flow (GPM) | Head (ft) | Flow (GPM) | Head (ft)
|  | 1920 | 67 | 1824 | 60.4675 | 1728 | 54.27 | 1632 | 48.4075 | 1536 | 42.88 | 1440 | 37.6875 | 1344 | 32.83 | 1248 | 28.3075 | 1152 | 24.12 | 1056 | 20.2675 | 960 | 16.75
|  | 2880 | 56.7 | 2736 | 51.1718 | 2592 | 45.927 | 2448 | 40.9657 | 2304 | 36.288 | 2160 | 31.8938 | 2016 | 27.783 | 1872 | 23.9558 | 1728 | 20.412 | 1584 | 17.1518 | 1440 | 14.175
|  | 3840 | 46 | 3648 | 41.515 | 3456 | 37.26 | 3264 | 33.235 | 3072 | 29.44 | 2880 | 25.875 | 2688 | 22.54 | 2496 | 19.435 | 2304 | 16.56 | 2112 | 13.915 | 1920 | 11.5
|  | 4800 | 35.5 | 4560 | 32.0388 | 4320 | 28.755 | 4080 | 25.6487 | 3840 | 22.72 | 3600 | 19.9688 | 3360 | 17.395 | 3120 | 14.9987 | 2880 | 12.78 | 2640 | 10.7388 | 2400 | 8.875
|  | 5760 | 23.2 | 5472 | 20.938 | 5184 | 18.792 | 4896 | 16.762 | 4608 | 14.848 | 4320 | 13.05 | 4032 | 11.368 | 3744 | 9.802 | 3456 | 8.352 | 3168 | 7.018 | 2880 | 5.8
Pumping Unit Data
Pump curve minus suction and individual discharge fitting losses
Note: Values calculated from affinity laws. Values in red are outside the recommended performance envelope. Values are not derated for header loss
| Single Pump | 100% | Max | 95% | Max | 90% | Max | 85% | Max | 80% | Max | 75% | Max | 70% | Max | 65% | Max | 60% | Max | 55% | Max | 50% | Max
|  | 1900 | RPM | 1805 | RPM | 1710 | RPM | 1615 | RPM | 1520 | RPM | 1425 | RPM | 1330 | RPM | 1235 | RPM | 1140 | RPM | 1045 | RPM | 950 | RPM
|  | Flow (GPM) | Head (ft) | Flow (GPM) | Head (ft) | Flow (GPM) | Head (ft) | Flow (GPM) | Head (ft) | Flow (GPM) | Head (ft) | Flow (GPM) | Head (ft) | Flow (GPM) | Head (ft) | Flow (GPM) | Head (ft) | Flow (GPM) | Head (ft) | Flow (GPM) | Head (ft) | Flow (GPM) | Head (ft)
|  | 960 | 66.0346 | 912 | 59.596 | 864 | 53.4875 | 816 | 47.7093 | 768 | 42.2613 | 720 | 37.1435 | 672 | 32.3559 | 624 | 27.8986 | 576 | 23.7714 | 528 | 19.9744 | 480 | 16.5076
|  | 1440 | 54.5327 | 1368 | 49.2152 | 1296 | 44.1705 | 1224 | 39.3985 | 1152 | 34.8992 | 1080 | 30.6727 | 1008 | 26.7189 | 936 | 23.0379 | 864 | 19.6295 | 792 | 16.4939 | 720 | 13.631
|  | 1920 | 42.1529 | 1824 | 38.0421 | 1728 | 34.1422 | 1632 | 30.4531 | 1536 | 26.975 | 1440 | 23.7077 | 1344 | 20.6513 | 1248 | 17.8059 | 1152 | 15.1712 | 1056 | 12.7475 | 960 | 10.5346
|  | 2400 | 29.4958 | 2280 | 26.6186 | 2160 | 23.889 | 2040 | 21.3071 | 1920 | 18.8729 | 1800 | 16.5864 | 1680 | 14.4475 | 1560 | 12.4563 | 1440 | 10.6127 | 1320 | 8.9168 | 1200 | 7.3684
|  | 2880 | 14.5618 | 2736 | 13.1401 | 2592 | 11.7914 | 2448 | 10.5159 | 2304 | 9.3134 | 2160 | 8.184 | 2016 | 7.1277 | 1872 | 6.1444 | 1728 | 5.2342 | 1584 | 4.3969 | 1440 | 3.6327
| Dual Pump | 100% | Max | 95% | Max | 90% | Max | 85% | Max | 80% | Max | 75% | Max | 70% | Max | 65% | Max | 60% | Max | 55% | Max | 50% | Max
|  | 1900 | RPM | 1805 | RPM | 1710 | RPM | 1615 | RPM | 1520 | RPM | 1425 | RPM | 1330 | RPM | 1235 | RPM | 1140 | RPM | 1045 | RPM | 950 | RPM
|  | Flow (GPM) | Head (ft) | Flow (GPM) | Head (ft) | Flow (GPM) | Head (ft) | Flow (GPM) | Head (ft) | Flow (GPM) | Head (ft) | Flow (GPM) | Head (ft) | Flow (GPM) | Head (ft) | Flow (GPM) | Head (ft) | Flow (GPM) | Head (ft) | Flow (GPM) | Head (ft) | Flow (GPM) | Head (ft)
|  | 1920 | 67 | 1824 | 59.596 | 1728 | 53.4875 | 1632 | 47.7093 | 1536 | 42.2613 | 1440 | 37.1435 | 1344 | 32.3559 | 1248 | 27.8986 | 1152 | 23.7714 | 1056 | 19.9744 | 960 | 16.5076
|  | 2880 | 56.7 | 2736 | 49.2152 | 2592 | 44.1705 | 2448 | 39.3985 | 2304 | 34.8992 | 2160 | 30.6727 | 2016 | 26.7189 | 1872 | 23.0379 | 1728 | 19.6295 | 1584 | 16.4939 | 1440 | 13.631
|  | 3840 | 46 | 3648 | 38.0421 | 3456 | 34.1422 | 3264 | 30.4531 | 3072 | 26.975 | 2880 | 23.7077 | 2688 | 20.6513 | 2496 | 17.8059 | 2304 | 15.1712 | 2112 | 12.7475 | 1920 | 10.5346
|  | 4800 | 35.5 | 4560 | 26.6186 | 4320 | 23.889 | 4080 | 21.3071 | 3840 | 18.8729 | 3600 | 16.5864 | 3360 | 14.4475 | 3120 | 12.4563 | 2880 | 10.6127 | 2640 | 8.9168 | 2400 | 7.3684
|  | 5760 | 23.2 | 5472 | 13.1401 | 5184 | 11.7914 | 4896 | 10.5159 | 4608 | 9.3134 | 4320 | 8.184 | 4032 | 7.1277 | 3744 | 6.1444 | 3456 | 5.2342 | 3168 | 4.3969 | 2880 | 3.6327
|  | Lower Bound |  | Upper Bound |  |  | Series Labels
|  | Q | H | Q | H
|  | 960 | 66.0346 | 2880 | 14.5618 |  | 1900 | 1900 rpm
|  | 912 | 59.596 | 2736 | 13.1401 |  | 1805 | 1805 rpm
|  | 864 | 53.4875 | 2592 | 11.7914 |  | 1710 | 1710 rpm
|  | 816 | 47.7093 | 2448 | 10.5159 |  | 1615 | 1615 rpm
|  | 768 | 42.2613 | 2304 | 9.3134 |  | 1520 | 1520 rpm
|  | 720 | 37.1435 | 2160 | 8.184 |  | 1425 | 1425 rpm
|  | 672 | 32.3559 | 2016 | 7.1277 |  | 1330 | 1330 rpm
|  | 624 | 27.8986 | 1872 | 6.1444 |  | 1235 | 1235 rpm
|  | 576 | 23.7714 | 1728 | 5.2342 |  | 1140 | 1140 rpm
|  | 528 | 19.9744 | 1584 | 4.3969 |  | 1045 | 1045 rpm
|  | 480 | 16.5076 | 1440 | 3.6327 |  | 950 | 950 rpm

## Pump Curve
| Pump Curve Input | [11 empty] | BEP Chart |  |  | AOR Chart
| Instructions: Input data to shaded cells only. Remaining cells are calculated. | [11 empty] | x | y |  | x | y
| Pump Info | Make | [10 empty] | 0 | 0 | 1 | 0 | 0
|  | Model | [10 empty] | 0.0001 | 100 | 2 | 0 | 50
|  | Impeller Size |  | in | [10 empty] | 3 | 0 | 0
|  | BEP |  | GPM | [10 empty] | 4 | 0 | 50
|  | POR | 0 | 0 | GPM | [9 empty] | 5 | 0 | 0
| Manufacturer's Pump Curve | Head(ft) | Flow, GPM (1 Pump) | Flow, GPM (2 Pumps) | Derated Values (w/ Header Loss) | [9 empty] | 6 | 0 | 50
[5 empty] | Head | 1 Pump, GPM | 2 Pump, GPM | [7 empty] | 7 | 0 | 0
|  | 58 | 0 | 0 | 58 | 0 | 0 | [7 empty] | 8 | 0 | 50
|  | 49 | 840 | 1680 | 48.651 | 840 | 1680 | [7 empty] | 9 | 0 | 0
|  | 44.1 | 1260 | 2520 | 43.3167 | 1260 | 2520 | [7 empty] | 10 | 0 | 50
|  | 38.6 | 1680 | 3360 | 37.2098 | 1680 | 3360 | [7 empty] | 11 | 0 | 0
|  | 32.7 | 2100 | 4200 | 30.5306 | 2100 | 4200 | [7 empty] | 12 | 0 | 50
|  | 26.2 | 2520 | 5040 | 23.0791 | 2520 | 5040 | [7 empty] | 13 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | [7 empty] | 14 | 0 | 50
|  |  |  | 0 | 0 | 0 | 0 | [7 empty] | 15 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | [7 empty] | 16 | 0 | 50
| Mfr's NPSHr Curve | NPSHr, ft | Flow, GPM (1 pump) | Safe NPSHr, ft | [10 empty] | 17 | 0 | 0
|  |  |  | 0 | [10 empty] | 18 | 0 | 50
|  |  |  | 0 |  |  |  | Select values for this column | [6 empty] | 19 | 0 | 0
|  |  |  | 0 |  |  |  | from sum of suction losses | [6 empty] | 20 | 0 | 50
|  |  |  | 0 |  |  |  | on the System Curve tab | [6 empty] | 21 | 0 | 0
|  |  |  | 0 | [10 empty] | 22 | 0 | 50
| Calculated NPSHa Curve @ Sea Level and 40° F | Operating Point | WW Level (NAVD88) | Flow, GPM | Hatm | Hsub | Hvp | HL | NPSHA | [5 empty] | 23 | 0 | 0
|  | Lead off | -14.18 | 0 | 33.96 | -0.28 | 0.3 |  | 33.38 | [5 empty] | 24 | 0 | 50
|  | Lead on | -6.95 | 0 | 33.96 | 6.95 | 0.3 |  | 40.61 | [5 empty] | 25 | 0 | 0
|  | LeadLag off | -14.18 | 0 | 33.96 | -0.28 | 0.3 |  | 33.38 |  | npshr coefficients |  |  |  | 26 | 0 | 50
|  | LeadLag on | -6.6 | 0 | 33.96 | 7.3 | 0.3 |  | 40.96 |  | c3 | #VALUE! |  |  | 27 | 0 | 0
|  | Overflow | 6.61 | 0 | 33.96 | 20.51 | 0.3 |  | 54.17 |  | c2 | #VALUE! |  |  | 28 | 0 | 50
[11 empty] | c1 | #VALUE! |  |  | 29 | 0 | 0
[11 empty] | b | #VALUE! |  |  | 30 | 0 | 50
[15 empty] | 31 | 0 | 0
| Affinity Law Calculator | [13 empty] | 32 | 0 | 50
| Use to generate pump curves for a specific impeller diameter from a given diameter. Use the closest available curve. | [13 empty] | 33 | 0 | 0
| ***Works only with constant casing and speed*** | [13 empty] | 34 | 0 | 50
|  | Given Impeller | 12 | in | [10 empty] | 35 | 0 | 0
|  | Target Impeller | 12.5 | in | [10 empty] | 36 | 0 | 50
|  | Given Impeller |  |  | Target Impeller | [9 empty] | 37 | 0 | 0
|  | Head (ft) | Flow (GPM) | Efficiency (%) | Head (ft) | Flow (GPM) | Efficiency(%) | [7 empty] | 38 | 0 | 50
[5 empty] | 0 | 0 | 0.8131% | [7 empty] | 39 | 0 | 0
[5 empty] | 0 | 0 | 0.8131% | [7 empty] | 40 | 0 | 50
[5 empty] | 0 | 0 | 0.8131% | [7 empty] | 41 | 0 | 0
[5 empty] | 0 | 0 | 0.8131% | [7 empty] | 42 | 0 | 50
[5 empty] | 0 | 0 | 0.8131% | [7 empty] | 43 | 0 | 0
[5 empty] | 0 | 0 | 0.8131% | [7 empty] | 44 | 0 | 50
[5 empty] | 0 | 0 | 0.8131% | [7 empty] | 45 | 0 | 0
[5 empty] | 0 | 0 | 0.8131% | [7 empty] | 46 | 0 | 50
[5 empty] | 0 | 0 | 0.8131% | [7 empty] | 47 | 0 | 0
[5 empty] | 0 | 0 | 0.8131% | [7 empty] | 48 | 0 | 50
[15 empty] | 49 | 0 | 0
[15 empty] | 50 | 0 | 50
[15 empty] | 51 | 0 | 0
[15 empty] | 52 | 0 | 50
[15 empty] | 53 | 0 | 0
[15 empty] | 54 | 0 | 50
[15 empty] | 55 | 0 | 0
[15 empty] | 56 | 0 | 50
[15 empty] | 57 | 0 | 0
[15 empty] | 58 | 0 | 50
[15 empty] | 59 | 0 | 0
[15 empty] | 60 | 0 | 50
[15 empty] | 61 | 0 | 0
[15 empty] | 62 | 0 | 50
[15 empty] | 63 | 0 | 0
[15 empty] | 64 | 0 | 50
[15 empty] | 65 | 0 | 0
| Calculations for Pump Derating | [13 empty] | 66 | 0 | 50
[15 empty] | 67 | 0 | 0
|  | Minor Loss of Individual Discharge Fittings | [12 empty] | 68 | 0 | 50
|  | 6x8 Ell | SCV | Plug V | 8x10 Ell | Tee-Line | Tee-Line | [7 empty] | 69 | 0 | 0
| Size, in | 8 | 12 | 12 | 12 | 12 | 12 | [7 empty] | 70 | 0 | 50
| K | 0.75 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | Sum of Minor Losses, ft | Friction Loss, ft | Total Loss, ft |  |  |  |  | 71 | 0 | 0
Flow, GPM | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 72 | 0 | 50
| 840 | 0.33452 | 3.537e-08 | 3.954e-22 | 4.9414e-50 | 7.7175e-106 | 1.8825e-217 | 0.33452 | 0.014443 | 0.34897 |  |  |  |  | 73 | 0 | 0
| 1260 | 0.75268 | 1.7906e-07 | 1.0134e-20 | 3.2457e-47 | 3.3296e-100 | 3.504e-206 | 0.75268 | 0.030578 | 0.78326 |  |  |  |  | 74 | 0 | 50
| 1680 | 1.3381 | 5.6591e-07 | 1.0122e-19 | 3.2384e-45 | 3.3146e-96 | 3.4725e-198 | 1.3381 | 0.052066 | 1.3902 |  |  |  |  | 75 | 0 | 0
| 2100 | 2.0908 | 1.3816e-06 | 6.0333e-19 | 1.1505e-43 | 4.1837e-93 | 5.5321e-192 | 2.0908 | 0.078675 | 2.1694 |  |  |  |  | 76 | 0 | 50
| 2520 | 3.0107 | 2.8649e-06 | 2.5942e-18 | 2.1271e-42 | 1.4301e-90 | 6.4638e-187 | 3.0107 | 0.11024 | 3.1209 |  |  |  |  | 77 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 78 | 0 | 50
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 79 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 80 | 0 | 50
[15 empty] | 81 | 0 | 0
[15 empty] | 82 | 0 | 50
[15 empty] | 83 | 0 | 0
[15 empty] | 84 | 0 | 50
[15 empty] | 85 | 0 | 0
[15 empty] | 86 | 0 | 50
[15 empty] | 87 | 0 | 0
[15 empty] | 88 | 0 | 50
[15 empty] | 89 | 0 | 0
[15 empty] | 90 | 0 | 50
[15 empty] | 91 | 0 | 0
[15 empty] | 92 | 0 | 50
[15 empty] | 93 | 0 | 0
[15 empty] | 94 | 0 | 50
[15 empty] | 95 | 0 | 0
[15 empty] | 96 | 0 | 50
[15 empty] | 97 | 0 | 0
[15 empty] | 98 | 0 | 50
[15 empty] | 99 | 0 | 0
[15 empty] | 100 | 0 | 50
[15 empty] | 101 | 0 | 0
[15 empty] | 102 | 0 | 50
[15 empty] | 103 | 0 | 0
[15 empty] | 104 | 0 | 50
[15 empty] | 105 | 0 | 0
[15 empty] | 106 | 0 | 50
[15 empty] | 107 | 0 | 0
[15 empty] | 108 | 0 | 50
[15 empty] | 109 | 0 | 0
[15 empty] | 110 | 0 | 50
[15 empty] | 111 | 0 | 0
[15 empty] | 112 | 0 | 50
[15 empty] | 113 | 0 | 0
[15 empty] | 114 | 0 | 50
[15 empty] | 115 | 0 | 0
[15 empty] | 116 | 0 | 50
[15 empty] | 117 | 0 | 0
[15 empty] | 118 | 0 | 50
[15 empty] | 119 | 0 | 0
[15 empty] | 120 | 0 | 50
[15 empty] | 121 | 0 | 0
[15 empty] | 122 | 0 | 50
[15 empty] | 123 | 0 | 0
[15 empty] | 124 | 0 | 50
[15 empty] | 125 | 0 | 0
[15 empty] | 126 | 0 | 50
[15 empty] | 127 | 0 | 0
[15 empty] | 128 | 0 | 50
[15 empty] | 129 | 0 | 0
[15 empty] | 130 | 0 | 50
[15 empty] | 131 | 0 | 0
[15 empty] | 132 | 0 | 50
[15 empty] | 133 | 0 | 0
[15 empty] | 134 | 0 | 50
[15 empty] | 135 | 0 | 0
[15 empty] | 136 | 0 | 50
[15 empty] | 137 | 0 | 0
[15 empty] | 138 | 0 | 50
[15 empty] | 139 | 0 | 0
[15 empty] | 140 | 0 | 50
[15 empty] | 141 | 0 | 0
[15 empty] | 142 | 0 | 50
[15 empty] | 143 | 0 | 0
[15 empty] | 144 | 0 | 50
[15 empty] | 145 | 0 | 0
[15 empty] | 146 | 0 | 50
[15 empty] | 147 | 0 | 0
[15 empty] | 148 | 0 | 50
[15 empty] | 149 | 0 | 0
[15 empty] | 150 | 0 | 50
[15 empty] | 151 | 0 | 0
[15 empty] | 152 | 0 | 50
[15 empty] | 153 | 0 | 0
[15 empty] | 154 | 0 | 50
[15 empty] | 155 | 0 | 0
[15 empty] | 156 | 0 | 50
[15 empty] | 157 | 0 | 0
[15 empty] | 158 | 0 | 50
[15 empty] | 159 | 0 | 0
[15 empty] | 160 | 0 | 50
[15 empty] | 161 | 0 | 0
[15 empty] | 162 | 0 | 50
[15 empty] | 163 | 0 | 0
[15 empty] | 164 | 0 | 50
[15 empty] | 165 | 0 | 0
[15 empty] | 166 | 0 | 50
[15 empty] | 167 | 0 | 0
[15 empty] | 168 | 0 | 50
[15 empty] | 169 | 0 | 0
[15 empty] | 170 | 0 | 50
[15 empty] | 171 | 0 | 0
[15 empty] | 172 | 0 | 50
[15 empty] | 173 | 0 | 0
[15 empty] | 174 | 0 | 50
[15 empty] | 175 | 0 | 0
[15 empty] | 176 | 0 | 50
[15 empty] | 177 | 0 | 0
[15 empty] | 178 | 0 | 50
[15 empty] | 179 | 0 | 0
[15 empty] | 180 | 0 | 50
[15 empty] | 181 | 0 | 0
[15 empty] | 182 | 0 | 50
[15 empty] | 183 | 0 | 0
[15 empty] | 184 | 0 | 50
[15 empty] | 185 | 0 | 0
[15 empty] | 186 | 0 | 50
[15 empty] | 187 | 0 | 0
[15 empty] | 188 | 0 | 50
[15 empty] | 189 | 0 | 0
[15 empty] | 190 | 0 | 50
[15 empty] | 191 | 0 | 0
[15 empty] | 192 | 0 | 50
[15 empty] | 193 | 0 | 0
[15 empty] | 194 | 0 | 50
[15 empty] | 195 | 0 | 0
[15 empty] | 196 | 0 | 50
[15 empty] | 197 | 0 | 0
[15 empty] | 198 | 0 | 50
[15 empty] | 199 | 0 | 0
[15 empty] | 200 | 0 | 50
[15 empty] | 201 | 0 | 0
[15 empty] | 202 | 0 | 50
[15 empty] | 203 | 0 | 0
[15 empty] | 204 | 0 | 50
[15 empty] | 205 | 0 | 0
[15 empty] | 206 | 0 | 50
[15 empty] | 207 | 0 | 0
[15 empty] | 208 | 0 | 50
[15 empty] | 209 | 0 | 0
[15 empty] | 210 | 0 | 50
[15 empty] | 211 | 0 | 0
[15 empty] | 212 | 0 | 50
[15 empty] | 213 | 0 | 0
[15 empty] | 214 | 0 | 50
[15 empty] | 215 | 0 | 0
[15 empty] | 216 | 0 | 50
[15 empty] | 217 | 0 | 0
[15 empty] | 218 | 0 | 50
[15 empty] | 219 | 0 | 0
[15 empty] | 220 | 0 | 50
[15 empty] | 221 | 0 | 0
[15 empty] | 222 | 0 | 50
[15 empty] | 223 | 0 | 0
[15 empty] | 224 | 0 | 50
[15 empty] | 225 | 0 | 0
[15 empty] | 226 | 0 | 50
[15 empty] | 227 | 0 | 0
[15 empty] | 228 | 0 | 50
[15 empty] | 229 | 0 | 0
[15 empty] | 230 | 0 | 50
[15 empty] | 231 | 0 | 0
[15 empty] | 232 | 0 | 50
[15 empty] | 233 | 0 | 0
[15 empty] | 234 | 0 | 50
[15 empty] | 235 | 0 | 0
[15 empty] | 236 | 0 | 50
[15 empty] | 237 | 0 | 0
[15 empty] | 238 | 0 | 50
[15 empty] | 239 | 0 | 0
[15 empty] | 240 | 0 | 50
[15 empty] | 241 | 0 | 0
[15 empty] | 242 | 0 | 50
[15 empty] | 243 | 0 | 0
[15 empty] | 244 | 0 | 50
[15 empty] | 245 | 0 | 0
[15 empty] | 246 | 0 | 50
[15 empty] | 247 | 0 | 0
[15 empty] | 248 | 0 | 50
[15 empty] | 249 | 0 | 0
[15 empty] | 250 | 0 | 50
[15 empty] | 251 | 0 | 0
[15 empty] | 252 | 0 | 50
[15 empty] | 253 | 0 | 0
[15 empty] | 254 | 0 | 50
[15 empty] | 255 | 0 | 0
[15 empty] | 256 | 0 | 50
[15 empty] | 257 | 0 | 0
[15 empty] | 258 | 0 | 50
[15 empty] | 259 | 0 | 0
[15 empty] | 260 | 0 | 50
[15 empty] | 261 | 0 | 0
[15 empty] | 262 | 0 | 50
[15 empty] | 263 | 0 | 0
[15 empty] | 264 | 0 | 50
[15 empty] | 265 | 0 | 0
[15 empty] | 266 | 0 | 50
[15 empty] | 267 | 0 | 0
[15 empty] | 268 | 0 | 50
[15 empty] | 269 | 0 | 0
[15 empty] | 270 | 0 | 50
[15 empty] | 271 | 0 | 0
[15 empty] | 272 | 0 | 50
[15 empty] | 273 | 0 | 0
[15 empty] | 274 | 0 | 50
[15 empty] | 275 | 0 | 0
[15 empty] | 276 | 0 | 50
[15 empty] | 277 | 0 | 0
[15 empty] | 278 | 0 | 50
[15 empty] | 279 | 0 | 0
[15 empty] | 280 | 0 | 50
[15 empty] | 281 | 0 | 0
[15 empty] | 282 | 0 | 50
[15 empty] | 283 | 0 | 0
[15 empty] | 284 | 0 | 50
[15 empty] | 285 | 0 | 0
[15 empty] | 286 | 0 | 50
[15 empty] | 287 | 0 | 0
[15 empty] | 288 | 0 | 50
[15 empty] | 289 | 0 | 0
[15 empty] | 290 | 0 | 50
[15 empty] | 291 | 0 | 0
[15 empty] | 292 | 0 | 50
[15 empty] | 293 | 0 | 0
[15 empty] | 294 | 0 | 50
[15 empty] | 295 | 0 | 0
[15 empty] | 296 | 0 | 50
[15 empty] | 297 | 0 | 0
[15 empty] | 298 | 0 | 50
[15 empty] | 299 | 0 | 0
[15 empty] | 300 | 0 | 50
[15 empty] | 301 | 0 | 0
[15 empty] | 302 | 0 | 50
[15 empty] | 303 | 0 | 0
[15 empty] | 304 | 0 | 50
[15 empty] | 305 | 0 | 0
[15 empty] | 306 | 0 | 50
[15 empty] | 307 | 0 | 0
[15 empty] | 308 | 0 | 50
[15 empty] | 309 | 0 | 0
[15 empty] | 310 | 0 | 50
[15 empty] | 311 | 0 | 0
[15 empty] | 312 | 0 | 50
[15 empty] | 313 | 0 | 0
[15 empty] | 314 | 0 | 50
[15 empty] | 315 | 0 | 0
[15 empty] | 316 | 0 | 50
[15 empty] | 317 | 0 | 0
[15 empty] | 318 | 0 | 50
[15 empty] | 319 | 0 | 0
[15 empty] | 320 | 0 | 50
[15 empty] | 321 | 0 | 0
[15 empty] | 322 | 0 | 50
[15 empty] | 323 | 0 | 0
[15 empty] | 324 | 0 | 50
[15 empty] | 325 | 0 | 0
[15 empty] | 326 | 0 | 50
[15 empty] | 327 | 0 | 0
[15 empty] | 328 | 0 | 50
[15 empty] | 329 | 0 | 0
[15 empty] | 330 | 0 | 50
[15 empty] | 331 | 0 | 0
[15 empty] | 332 | 0 | 50
[15 empty] | 333 | 0 | 0
[15 empty] | 334 | 0 | 50
[15 empty] | 335 | 0 | 0
[15 empty] | 336 | 0 | 50
[15 empty] | 337 | 0 | 0
[15 empty] | 338 | 0 | 50
[15 empty] | 339 | 0 | 0
[15 empty] | 340 | 0 | 50
[15 empty] | 341 | 0 | 0
[15 empty] | 342 | 0 | 50
[15 empty] | 343 | 0 | 0
[15 empty] | 344 | 0 | 50
[15 empty] | 345 | 0 | 0
[15 empty] | 346 | 0 | 50
[15 empty] | 347 | 0 | 0
[15 empty] | 348 | 0 | 50
[15 empty] | 349 | 0 | 0
[15 empty] | 350 | 0 | 50
[15 empty] | 351 | 0 | 0
[15 empty] | 352 | 0 | 50
[15 empty] | 353 | 0 | 0
[15 empty] | 354 | 0 | 50
[15 empty] | 355 | 0 | 0
[15 empty] | 356 | 0 | 50
[15 empty] | 357 | 0 | 0
[15 empty] | 358 | 0 | 50
[15 empty] | 359 | 0 | 0
[15 empty] | 360 | 0 | 50
[15 empty] | 361 | 0 | 0
[15 empty] | 362 | 0 | 50
[15 empty] | 363 | 0 | 0
[15 empty] | 364 | 0 | 50
[15 empty] | 365 | 0 | 0
[15 empty] | 366 | 0 | 50
[15 empty] | 367 | 0 | 0
[15 empty] | 368 | 0 | 50
[15 empty] | 369 | 0 | 0
[15 empty] | 370 | 0 | 50
[15 empty] | 371 | 0 | 0
[15 empty] | 372 | 0 | 50
[15 empty] | 373 | 0 | 0
[15 empty] | 374 | 0 | 50
[15 empty] | 375 | 0 | 0
[15 empty] | 376 | 0 | 50
[15 empty] | 377 | 0 | 0
[15 empty] | 378 | 0 | 50
[15 empty] | 379 | 0 | 0
[15 empty] | 380 | 0 | 50
[15 empty] | 381 | 0 | 0
[15 empty] | 382 | 0 | 50
[15 empty] | 383 | 0 | 0
[15 empty] | 384 | 0 | 50
[15 empty] | 385 | 0 | 0
[15 empty] | 386 | 0 | 50
[15 empty] | 387 | 0 | 0
[15 empty] | 388 | 0 | 50
[15 empty] | 389 | 0 | 0
[15 empty] | 390 | 0 | 50
[15 empty] | 391 | 0 | 0
[15 empty] | 392 | 0 | 50
[15 empty] | 393 | 0 | 0
[15 empty] | 394 | 0 | 50
[15 empty] | 395 | 0 | 0
[15 empty] | 396 | 0 | 50
[15 empty] | 397 | 0 | 0
[15 empty] | 398 | 0 | 50
[15 empty] | 399 | 0 | 0
[15 empty] | 400 | 0 | 50
[15 empty] | 401 | 0 | 0
[15 empty] | 402 | 0 | 50
[15 empty] | 403 | 0 | 0
[15 empty] | 404 | 0 | 50
[15 empty] | 405 | 0 | 0
[15 empty] | 406 | 0 | 50
[15 empty] | 407 | 0 | 0
[15 empty] | 408 | 0 | 50
[15 empty] | 409 | 0 | 0
[15 empty] | 410 | 0 | 50
[15 empty] | 411 | 0 | 0
[15 empty] | 412 | 0 | 50
[15 empty] | 413 | 0 | 0
[15 empty] | 414 | 0 | 50
[15 empty] | 415 | 0 | 0
[15 empty] | 416 | 0 | 50
[15 empty] | 417 | 0 | 0
[15 empty] | 418 | 0 | 50
[15 empty] | 419 | 0 | 0
[15 empty] | 420 | 0 | 50
[15 empty] | 421 | 0 | 0
[15 empty] | 422 | 0 | 50
[15 empty] | 423 | 0 | 0
[15 empty] | 424 | 0 | 50
[15 empty] | 425 | 0 | 0
[15 empty] | 426 | 0 | 50
[15 empty] | 427 | 0 | 0
[15 empty] | 428 | 0 | 50
[15 empty] | 429 | 0 | 0
[15 empty] | 430 | 0 | 50
[15 empty] | 431 | 0 | 0
[15 empty] | 432 | 0 | 50
[15 empty] | 433 | 0 | 0
[15 empty] | 434 | 0 | 50
[15 empty] | 435 | 0 | 0
[15 empty] | 436 | 0 | 50
[15 empty] | 437 | 0 | 0
[15 empty] | 438 | 0 | 50
[15 empty] | 439 | 0 | 0
[15 empty] | 440 | 0 | 50
[15 empty] | 441 | 0 | 0
[15 empty] | 442 | 0 | 50
[15 empty] | 443 | 0 | 0
[15 empty] | 444 | 0 | 50
[15 empty] | 445 | 0 | 0
[15 empty] | 446 | 0 | 50
[15 empty] | 447 | 0 | 0
[15 empty] | 448 | 0 | 50
[15 empty] | 449 | 0 | 0
[15 empty] | 450 | 0 | 50
[15 empty] | 451 | 0 | 0
[15 empty] | 452 | 0 | 50
[15 empty] | 453 | 0 | 0
[15 empty] | 454 | 0 | 50
[15 empty] | 455 | 0 | 0
[15 empty] | 456 | 0 | 50
[15 empty] | 457 | 0 | 0
[15 empty] | 458 | 0 | 50
[15 empty] | 459 | 0 | 0
[15 empty] | 460 | 0 | 50
[15 empty] | 461 | 0 | 0
[15 empty] | 462 | 0 | 50
[15 empty] | 463 | 0 | 0
[15 empty] | 464 | 0 | 50
[15 empty] | 465 | 0 | 0
[15 empty] | 466 | 0 | 50
[15 empty] | 467 | 0 | 0
[15 empty] | 468 | 0 | 50
[15 empty] | 469 | 0 | 0
[15 empty] | 470 | 0 | 50
[15 empty] | 471 | 0 | 0
[15 empty] | 472 | 0 | 50
[15 empty] | 473 | 0 | 0
[15 empty] | 474 | 0 | 50
[15 empty] | 475 | 0 | 0
[15 empty] | 476 | 0 | 50
[15 empty] | 477 | 0 | 0
[15 empty] | 478 | 0 | 50
[15 empty] | 479 | 0 | 0
[15 empty] | 480 | 0 | 50
[15 empty] | 481 | 0 | 0
[15 empty] | 482 | 0 | 50
[15 empty] | 483 | 0 | 0
[15 empty] | 484 | 0 | 50
[15 empty] | 485 | 0 | 0
[15 empty] | 486 | 0 | 50
[15 empty] | 487 | 0 | 0
[15 empty] | 488 | 0 | 50
[15 empty] | 489 | 0 | 0
[15 empty] | 490 | 0 | 50
[15 empty] | 491 | 0 | 0
[15 empty] | 492 | 0 | 50
[15 empty] | 493 | 0 | 0
[15 empty] | 494 | 0 | 50
[15 empty] | 495 | 0 | 0
[15 empty] | 496 | 0 | 50
[15 empty] | 497 | 0 | 0
[15 empty] | 498 | 0 | 50
[15 empty] | 499 | 0 | 0
[15 empty] | 500 | 0 | 50
[15 empty] | 501 | 0 | 0
[15 empty] | 502 | 0 | 50
[15 empty] | 503 | 0 | 0
[15 empty] | 504 | 0 | 50
[15 empty] | 505 | 0 | 0
[15 empty] | 506 | 0 | 50
[15 empty] | 507 | 0 | 0
[15 empty] | 508 | 0 | 50
[15 empty] | 509 | 0 | 0
[15 empty] | 510 | 0 | 50
[15 empty] | 511 | 0 | 0
[15 empty] | 512 | 0 | 50
[15 empty] | 513 | 0 | 0
[15 empty] | 514 | 0 | 50
[15 empty] | 515 | 0 | 0
[15 empty] | 516 | 0 | 50
[15 empty] | 517 | 0 | 0
[15 empty] | 518 | 0 | 50
[15 empty] | 519 | 0 | 0
[15 empty] | 520 | 0 | 50
[15 empty] | 521 | 0 | 0
[15 empty] | 522 | 0 | 50
[15 empty] | 523 | 0 | 0
[15 empty] | 524 | 0 | 50
[15 empty] | 525 | 0 | 0
[15 empty] | 526 | 0 | 50
[15 empty] | 527 | 0 | 0
[15 empty] | 528 | 0 | 50
[15 empty] | 529 | 0 | 0
[15 empty] | 530 | 0 | 50
[15 empty] | 531 | 0 | 0
[15 empty] | 532 | 0 | 50
[15 empty] | 533 | 0 | 0
[15 empty] | 534 | 0 | 50
[15 empty] | 535 | 0 | 0
[15 empty] | 536 | 0 | 50
[15 empty] | 537 | 0 | 0
[15 empty] | 538 | 0 | 50
[15 empty] | 539 | 0 | 0
[15 empty] | 540 | 0 | 50
[15 empty] | 541 | 0 | 0
[15 empty] | 542 | 0 | 50
[15 empty] | 543 | 0 | 0
[15 empty] | 544 | 0 | 50
[15 empty] | 545 | 0 | 0
[15 empty] | 546 | 0 | 50
[15 empty] | 547 | 0 | 0
[15 empty] | 548 | 0 | 50
[15 empty] | 549 | 0 | 0
[15 empty] | 550 | 0 | 50
[15 empty] | 551 | 0 | 0
[15 empty] | 552 | 0 | 50
[15 empty] | 553 | 0 | 0
[15 empty] | 554 | 0 | 50
[15 empty] | 555 | 0 | 0
[15 empty] | 556 | 0 | 50
[15 empty] | 557 | 0 | 0
[15 empty] | 558 | 0 | 50
[15 empty] | 559 | 0 | 0
[15 empty] | 560 | 0 | 50
[15 empty] | 561 | 0 | 0
[15 empty] | 562 | 0 | 50
[15 empty] | 563 | 0 | 0
[15 empty] | 564 | 0 | 50
[15 empty] | 565 | 0 | 0
[15 empty] | 566 | 0 | 50
[15 empty] | 567 | 0 | 0
[15 empty] | 568 | 0 | 50
[15 empty] | 569 | 0 | 0
[15 empty] | 570 | 0 | 50
[15 empty] | 571 | 0 | 0
[15 empty] | 572 | 0 | 50
[15 empty] | 573 | 0 | 0
[15 empty] | 574 | 0 | 50
[15 empty] | 575 | 0 | 0
[15 empty] | 576 | 0 | 50
[15 empty] | 577 | 0 | 0
[15 empty] | 578 | 0 | 50
[15 empty] | 579 | 0 | 0
[15 empty] | 580 | 0 | 50
[15 empty] | 581 | 0 | 0
[15 empty] | 582 | 0 | 50
[15 empty] | 583 | 0 | 0
[15 empty] | 584 | 0 | 50
[15 empty] | 585 | 0 | 0
[15 empty] | 586 | 0 | 50
[15 empty] | 587 | 0 | 0
[15 empty] | 588 | 0 | 50
[15 empty] | 589 | 0 | 0
[15 empty] | 590 | 0 | 50
[15 empty] | 591 | 0 | 0
[15 empty] | 592 | 0 | 50
[15 empty] | 593 | 0 | 0
[15 empty] | 594 | 0 | 50
[15 empty] | 595 | 0 | 0
[15 empty] | 596 | 0 | 50
[15 empty] | 597 | 0 | 0
[15 empty] | 598 | 0 | 50
[15 empty] | 599 | 0 | 0
[15 empty] | 600 | 0 | 50
[15 empty] | 601 | 0 | 0
[15 empty] | 602 | 0 | 50
[15 empty] | 603 | 0 | 0
[15 empty] | 604 | 0 | 50
[15 empty] | 605 | 0 | 0
[15 empty] | 606 | 0 | 50
[15 empty] | 607 | 0 | 0
[15 empty] | 608 | 0 | 50
[15 empty] | 609 | 0 | 0
[15 empty] | 610 | 0 | 50
[15 empty] | 611 | 0 | 0
[15 empty] | 612 | 0 | 50
[15 empty] | 613 | 0 | 0
[15 empty] | 614 | 0 | 50
[15 empty] | 615 | 0 | 0
[15 empty] | 616 | 0 | 50
[15 empty] | 617 | 0 | 0
[15 empty] | 618 | 0 | 50
[15 empty] | 619 | 0 | 0
[15 empty] | 620 | 0 | 50
[15 empty] | 621 | 0 | 0
[15 empty] | 622 | 0 | 50
[15 empty] | 623 | 0 | 0
[15 empty] | 624 | 0 | 50
[15 empty] | 625 | 0 | 0
[15 empty] | 626 | 0 | 50
[15 empty] | 627 | 0 | 0
[15 empty] | 628 | 0 | 50
[15 empty] | 629 | 0 | 0
[15 empty] | 630 | 0 | 50
[15 empty] | 631 | 0 | 0
[15 empty] | 632 | 0 | 50
[15 empty] | 633 | 0 | 0
[15 empty] | 634 | 0 | 50
[15 empty] | 635 | 0 | 0
[15 empty] | 636 | 0 | 50
[15 empty] | 637 | 0 | 0
[15 empty] | 638 | 0 | 50
[15 empty] | 639 | 0 | 0
[15 empty] | 640 | 0 | 50
[15 empty] | 641 | 0 | 0
[15 empty] | 642 | 0 | 50
[15 empty] | 643 | 0 | 0
[15 empty] | 644 | 0 | 50
[15 empty] | 645 | 0 | 0
[15 empty] | 646 | 0 | 50
[15 empty] | 647 | 0 | 0
[15 empty] | 648 | 0 | 50
[15 empty] | 649 | 0 | 0
[15 empty] | 650 | 0 | 50
[15 empty] | 651 | 0 | 0
[15 empty] | 652 | 0 | 50
[15 empty] | 653 | 0 | 0
[15 empty] | 654 | 0 | 50
[15 empty] | 655 | 0 | 0
[15 empty] | 656 | 0 | 50
[15 empty] | 657 | 0 | 0
[15 empty] | 658 | 0 | 50
[15 empty] | 659 | 0 | 0
[15 empty] | 660 | 0 | 50
[15 empty] | 661 | 0 | 0
[15 empty] | 662 | 0 | 50
[15 empty] | 663 | 0 | 0
[15 empty] | 664 | 0 | 50
[15 empty] | 665 | 0 | 0
[15 empty] | 666 | 0 | 50
[15 empty] | 667 | 0 | 0
[15 empty] | 668 | 0 | 50
[15 empty] | 669 | 0 | 0
[15 empty] | 670 | 0 | 50
[15 empty] | 671 | 0 | 0
[15 empty] | 672 | 0 | 50
[15 empty] | 673 | 0 | 0
[15 empty] | 674 | 0 | 50
[15 empty] | 675 | 0 | 0
[15 empty] | 676 | 0 | 50
[15 empty] | 677 | 0 | 0
[15 empty] | 678 | 0 | 50
[15 empty] | 679 | 0 | 0
[15 empty] | 680 | 0 | 50
[15 empty] | 681 | 0 | 0
[15 empty] | 682 | 0 | 50
[15 empty] | 683 | 0 | 0
[15 empty] | 684 | 0 | 50
[15 empty] | 685 | 0 | 0
[15 empty] | 686 | 0 | 50
[15 empty] | 687 | 0 | 0
[15 empty] | 688 | 0 | 50
[15 empty] | 689 | 0 | 0
[15 empty] | 690 | 0 | 50
[15 empty] | 691 | 0 | 0
[15 empty] | 692 | 0 | 50
[15 empty] | 693 | 0 | 0
[15 empty] | 694 | 0 | 50
[15 empty] | 695 | 0 | 0
[15 empty] | 696 | 0 | 50
[15 empty] | 697 | 0 | 0
[15 empty] | 698 | 0 | 50
[15 empty] | 699 | 0 | 0
[15 empty] | 700 | 0 | 50
[15 empty] | 701 | 0 | 0
[15 empty] | 702 | 0 | 50
[15 empty] | 703 | 0 | 0
[15 empty] | 704 | 0 | 50
[15 empty] | 705 | 0 | 0
[15 empty] | 706 | 0 | 50
[15 empty] | 707 | 0 | 0
[15 empty] | 708 | 0 | 50
[15 empty] | 709 | 0 | 0
[15 empty] | 710 | 0 | 50
[15 empty] | 711 | 0 | 0
[15 empty] | 712 | 0 | 50
[15 empty] | 713 | 0 | 0
[15 empty] | 714 | 0 | 50
[15 empty] | 715 | 0 | 0
[15 empty] | 716 | 0 | 50
[15 empty] | 717 | 0 | 0
[15 empty] | 718 | 0 | 50
[15 empty] | 719 | 0 | 0
[15 empty] | 720 | 0 | 50
[15 empty] | 721 | 0 | 0
[15 empty] | 722 | 0 | 50
[15 empty] | 723 | 0 | 0
[15 empty] | 724 | 0 | 50
[15 empty] | 725 | 0 | 0
[15 empty] | 726 | 0 | 50
[15 empty] | 727 | 0 | 0
[15 empty] | 728 | 0 | 50
[15 empty] | 729 | 0 | 0
[15 empty] | 730 | 0 | 50
[15 empty] | 731 | 0 | 0
[15 empty] | 732 | 0 | 50
[15 empty] | 733 | 0 | 0
[15 empty] | 734 | 0 | 50
[15 empty] | 735 | 0 | 0
[15 empty] | 736 | 0 | 50
[15 empty] | 737 | 0 | 0
[15 empty] | 738 | 0 | 50
[15 empty] | 739 | 0 | 0
[15 empty] | 740 | 0 | 50
[15 empty] | 741 | 0 | 0
[15 empty] | 742 | 0 | 50
[15 empty] | 743 | 0 | 0
[15 empty] | 744 | 0 | 50
[15 empty] | 745 | 0 | 0
[15 empty] | 746 | 0 | 50
[15 empty] | 747 | 0 | 0
[15 empty] | 748 | 0 | 50
[15 empty] | 749 | 0 | 0
[15 empty] | 750 | 0 | 50
[15 empty] | 751 | 0 | 0
[15 empty] | 752 | 0 | 50
[15 empty] | 753 | 0 | 0
[15 empty] | 754 | 0 | 50
[15 empty] | 755 | 0 | 0
[15 empty] | 756 | 0 | 50
[15 empty] | 757 | 0 | 0
[15 empty] | 758 | 0 | 50
[15 empty] | 759 | 0 | 0
[15 empty] | 760 | 0 | 50
[15 empty] | 761 | 0 | 0
[15 empty] | 762 | 0 | 50
[15 empty] | 763 | 0 | 0
[15 empty] | 764 | 0 | 50
[15 empty] | 765 | 0 | 0
[15 empty] | 766 | 0 | 50
[15 empty] | 767 | 0 | 0
[15 empty] | 768 | 0 | 50
[15 empty] | 769 | 0 | 0
[15 empty] | 770 | 0 | 50
[15 empty] | 771 | 0 | 0
[15 empty] | 772 | 0 | 50
[15 empty] | 773 | 0 | 0
[15 empty] | 774 | 0 | 50
[15 empty] | 775 | 0 | 0
[15 empty] | 776 | 0 | 50
[15 empty] | 777 | 0 | 0
[15 empty] | 778 | 0 | 50
[15 empty] | 779 | 0 | 0
[15 empty] | 780 | 0 | 50
[15 empty] | 781 | 0 | 0
[15 empty] | 782 | 0 | 50
[15 empty] | 783 | 0 | 0
[15 empty] | 784 | 0 | 50
[15 empty] | 785 | 0 | 0
[15 empty] | 786 | 0 | 50
[15 empty] | 787 | 0 | 0
[15 empty] | 788 | 0 | 50
[15 empty] | 789 | 0 | 0
[15 empty] | 790 | 0 | 50
[15 empty] | 791 | 0 | 0
[15 empty] | 792 | 0 | 50
[15 empty] | 793 | 0 | 0
[15 empty] | 794 | 0 | 50
[15 empty] | 795 | 0 | 0
[15 empty] | 796 | 0 | 50
[15 empty] | 797 | 0 | 0
[15 empty] | 798 | 0 | 50
[15 empty] | 799 | 0 | 0
[15 empty] | 800 | 0 | 50
[15 empty] | 801 | 0 | 0
[15 empty] | 802 | 0 | 50
[15 empty] | 803 | 0 | 0
[15 empty] | 804 | 0 | 50
[15 empty] | 805 | 0 | 0
[15 empty] | 806 | 0 | 50
[15 empty] | 807 | 0 | 0
[15 empty] | 808 | 0 | 50
[15 empty] | 809 | 0 | 0
[15 empty] | 810 | 0 | 50
[15 empty] | 811 | 0 | 0
[15 empty] | 812 | 0 | 50
[15 empty] | 813 | 0 | 0
[15 empty] | 814 | 0 | 50
[15 empty] | 815 | 0 | 0
[15 empty] | 816 | 0 | 50
[15 empty] | 817 | 0 | 0
[15 empty] | 818 | 0 | 50
[15 empty] | 819 | 0 | 0
[15 empty] | 820 | 0 | 50
[15 empty] | 821 | 0 | 0
[15 empty] | 822 | 0 | 50
[15 empty] | 823 | 0 | 0
[15 empty] | 824 | 0 | 50
[15 empty] | 825 | 0 | 0
[15 empty] | 826 | 0 | 50
[15 empty] | 827 | 0 | 0
[15 empty] | 828 | 0 | 50
[15 empty] | 829 | 0 | 0
[15 empty] | 830 | 0 | 50
[15 empty] | 831 | 0 | 0
[15 empty] | 832 | 0 | 50
[15 empty] | 833 | 0 | 0
[15 empty] | 834 | 0 | 50
[15 empty] | 835 | 0 | 0
[15 empty] | 836 | 0 | 50
[15 empty] | 837 | 0 | 0
[15 empty] | 838 | 0 | 50
[15 empty] | 839 | 0 | 0
[15 empty] | 840 | 0 | 50
[15 empty] | 841 | 0 | 0
[15 empty] | 842 | 0 | 50
[15 empty] | 843 | 0 | 0
[15 empty] | 844 | 0 | 50
[15 empty] | 845 | 0 | 0
[15 empty] | 846 | 0 | 50
[15 empty] | 847 | 0 | 0
[15 empty] | 848 | 0 | 50
[15 empty] | 849 | 0 | 0
[15 empty] | 850 | 0 | 50
[15 empty] | 851 | 0 | 0
[15 empty] | 852 | 0 | 50
[15 empty] | 853 | 0 | 0
[15 empty] | 854 | 0 | 50
[15 empty] | 855 | 0 | 0
[15 empty] | 856 | 0 | 50
[15 empty] | 857 | 0 | 0
[15 empty] | 858 | 0 | 50
[15 empty] | 859 | 0 | 0
[15 empty] | 860 | 0 | 50
[15 empty] | 861 | 0 | 0
[15 empty] | 862 | 0 | 50
[15 empty] | 863 | 0 | 0
[15 empty] | 864 | 0 | 50
[15 empty] | 865 | 0 | 0
[15 empty] | 866 | 0 | 50
[15 empty] | 867 | 0 | 0
[15 empty] | 868 | 0 | 50
[15 empty] | 869 | 0 | 0
[15 empty] | 870 | 0 | 50
[15 empty] | 871 | 0 | 0
[15 empty] | 872 | 0 | 50
[15 empty] | 873 | 0 | 0
[15 empty] | 874 | 0 | 50
[15 empty] | 875 | 0 | 0
[15 empty] | 876 | 0 | 50
[15 empty] | 877 | 0 | 0
[15 empty] | 878 | 0 | 50
[15 empty] | 879 | 0 | 0
[15 empty] | 880 | 0 | 50
[15 empty] | 881 | 0 | 0
[15 empty] | 882 | 0 | 50
[15 empty] | 883 | 0 | 0
[15 empty] | 884 | 0 | 50
[15 empty] | 885 | 0 | 0
[15 empty] | 886 | 0 | 50
[15 empty] | 887 | 0 | 0
[15 empty] | 888 | 0 | 50
[15 empty] | 889 | 0 | 0
[15 empty] | 890 | 0 | 50
[15 empty] | 891 | 0 | 0
[15 empty] | 892 | 0 | 50
[15 empty] | 893 | 0 | 0
[15 empty] | 894 | 0 | 50
[15 empty] | 895 | 0 | 0
[15 empty] | 896 | 0 | 50
[15 empty] | 897 | 0 | 0
[15 empty] | 898 | 0 | 50
[15 empty] | 899 | 0 | 0
[15 empty] | 900 | 0 | 50
[15 empty] | 901 | 0 | 0
[15 empty] | 902 | 0 | 50
[15 empty] | 903 | 0 | 0
[15 empty] | 904 | 0 | 50
[15 empty] | 905 | 0 | 0
[15 empty] | 906 | 0 | 50
[15 empty] | 907 | 0 | 0
[15 empty] | 908 | 0 | 50
[15 empty] | 909 | 0 | 0
[15 empty] | 910 | 0 | 50
[15 empty] | 911 | 0 | 0
[15 empty] | 912 | 0 | 50
[15 empty] | 913 | 0 | 0
[15 empty] | 914 | 0 | 50
[15 empty] | 915 | 0 | 0
[15 empty] | 916 | 0 | 50
[15 empty] | 917 | 0 | 0
[15 empty] | 918 | 0 | 50
[15 empty] | 919 | 0 | 0
[15 empty] | 920 | 0 | 50
[15 empty] | 921 | 0 | 0
[15 empty] | 922 | 0 | 50
[15 empty] | 923 | 0 | 0
[15 empty] | 924 | 0 | 50
[15 empty] | 925 | 0 | 0
[15 empty] | 926 | 0 | 50
[15 empty] | 927 | 0 | 0
[15 empty] | 928 | 0 | 50
[15 empty] | 929 | 0 | 0
[15 empty] | 930 | 0 | 50
[15 empty] | 931 | 0 | 0
[15 empty] | 932 | 0 | 50
[15 empty] | 933 | 0 | 0
[15 empty] | 934 | 0 | 50
[15 empty] | 935 | 0 | 0
[15 empty] | 936 | 0 | 50
[15 empty] | 937 | 0 | 0
[15 empty] | 938 | 0 | 50
[15 empty] | 939 | 0 | 0
[15 empty] | 940 | 0 | 50
[15 empty] | 941 | 0 | 0
[15 empty] | 942 | 0 | 50
[15 empty] | 943 | 0 | 0
[15 empty] | 944 | 0 | 50
[15 empty] | 945 | 0 | 0
[15 empty] | 946 | 0 | 50
[15 empty] | 947 | 0 | 0
[15 empty] | 948 | 0 | 50
[15 empty] | 949 | 0 | 0
[15 empty] | 950 | 0 | 50
[15 empty] | 951 | 0 | 0
[15 empty] | 952 | 0 | 50
[15 empty] | 953 | 0 | 0
[15 empty] | 954 | 0 | 50
[15 empty] | 955 | 0 | 0
[15 empty] | 956 | 0 | 50
[15 empty] | 957 | 0 | 0
[15 empty] | 958 | 0 | 50
[15 empty] | 959 | 0 | 0
[15 empty] | 960 | 0 | 50
[15 empty] | 961 | 0 | 0
[15 empty] | 962 | 0 | 50
[15 empty] | 963 | 0 | 0
[15 empty] | 964 | 0 | 50
[15 empty] | 965 | 0 | 0
[15 empty] | 966 | 0 | 50
[15 empty] | 967 | 0 | 0
[15 empty] | 968 | 0 | 50
[15 empty] | 969 | 0 | 0
[15 empty] | 970 | 0 | 50
[15 empty] | 971 | 0 | 0
[15 empty] | 972 | 0 | 50
[15 empty] | 973 | 0 | 0
[15 empty] | 974 | 0 | 50
[15 empty] | 975 | 0 | 0
[15 empty] | 976 | 0 | 50
[15 empty] | 977 | 0 | 0
[15 empty] | 978 | 0 | 50
[15 empty] | 979 | 0 | 0
[15 empty] | 980 | 0 | 50
[15 empty] | 981 | 0 | 0
[15 empty] | 982 | 0 | 50
[15 empty] | 983 | 0 | 0
[15 empty] | 984 | 0 | 50
[15 empty] | 985 | 0 | 0
[15 empty] | 986 | 0 | 50
[15 empty] | 987 | 0 | 0
[15 empty] | 988 | 0 | 50
[15 empty] | 989 | 0 | 0
[15 empty] | 990 | 0 | 50
[15 empty] | 991 | 0 | 0
[15 empty] | 992 | 0 | 50
[15 empty] | 993 | 0 | 0
[15 empty] | 994 | 0 | 50
[15 empty] | 995 | 0 | 0
[15 empty] | 996 | 0 | 50
[15 empty] | 997 | 0 | 0
[15 empty] | 998 | 0 | 50
[15 empty] | 999 | 0 | 0
[15 empty] | 1000 | 0 | 50

## Pump Design Summary
Pump Station Design Summary Sheet
Station # | 072
Address | 2600 13th Ave SW
By | Jesse Nofziger, P.E.
Input operating points in shaded cells from pump curves
Station | Storage Volume, gal | 12306.096
| Inflow | Dry | Wet
|  | 800 | 300
| Storage Time, hr | 0.25638 | 0.68367
Pump | Make | 0
| Model | 0
| Impeller Size, in | 0
| BEP, GPM | 0
| Preferred Operating Range, GPM | Min | Max
|  | 0 | 0
Motor | Make
Model
Rated Capacity, HP
Max Speed
Efficiency
Force Main | Material | CI
| Hazen-Williams 'C' | 100
| Age | 51
| Diameter, in | 10
| Length, ft | 47.16
System Performance | Operating Point | Fill/Draw | Design Point | Max 1 Pump | Load Share | Max 2 Pump
| Static Head, ft | 22.8 | 15.57 | 22.8 | 15.22 | 2.01
Total Head, ft
Flow, GPM
Speed, rpm
| % of BEP | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| Velocity, ft/s | 0 | 0 | 0 | 0 | 0
| NPSHr, ft | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| NPSHa, ft | 33.38 | 40.61 | 33.38 | 40.96 | 54.17
Pump Efficiency, %
| Pump BHP, HP | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| % Of Motor Capacity | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| System Efficiency | 0% | 0% | 0% | 0% | 0%
Assumptions for Analysis:
[7 empty] | chart title | Pump Station #072 Pump Curves: 0 0 Pumps, 0 in. Impeller, 10 in. CI Force Main, C=100
Pump Station #
Pump Curves:
Pumps,
Force Main,
C=
Impeller,
in.